## Calculator
HEAD LOSS THROUGH LINEAR LENGTH OF PIPE
| HR PUMP FLOW | 30 | IGPM
| PRESSURE (BAR) AT OUTLET | 66.91 | FT HEAD
| TYPE OF PIPE | Ductile Iron (DI)
| LENGTH OF PIPE | 18288 | MM
|  | 60 | FT
| SELECTED TYPE | Cast Iron (CI)
| C-VALUE | 100
| DIAMETER OF PIPE (INTERNAL DIAMETER) | 2 | INCH
| HEAD LOSS THROUGH Linear Length of Pipe (FT) | 3.2508 | FT
HEAD LOSS THROUGH PIPE FITTINGS
No. of Fitting | Fitting Type | Loss (ft) | Meter | Total
10 | Elbow 90°- Threaded/Screwed R/D = 1 (Std.) | 5.8333 | 1.7785 | 58.3333
2 | Tee- T-Through branch (Main-main Converge/Main-main Diverge) | 10 | 3.0488 | 20
2 | Tee- T-Through run (Main-branch Converge/Diverge) | 3.3333 | 1.0163 | 6.6667
1 | Alarm/Check Valve (Swing Type) | 16.6667 | 5.0813 | 16.6667
1 | Gate Valve (Full Open/Straight Way) | 2.1667 | 0.66057 | 2.1667
1 | Hose Coupling | 0.83333 | 0.25407 | 0.83333
Select Fitting Type
Select Fitting Type
Select Fitting Type
Select Fitting Type
Select Fitting Type
Select Fitting Type
Select Fitting Type
Select Fitting Type
Select Fitting Type
| HEIGHT OF FURTHEST DISCHARGE AGAINST GRAVITY | 30 | feet
| TOTAL SYSTEM LOSS | 137.9175 | feet
| PUMP SELECTION | 225.3102 | feet

## Fittings
Full Name of Fitting | Fitting | Type | Turn Radius (if any) | Sources of Reference
|  |  |  | Wolfram | Neutrium.net | MS (avg) | Katmar | jensapardi.files | Design/ Selection
Elbow 90°- Threaded/Screwed R/D = 1 (Std.) | Elbow 90° | Threaded/Screwed | R/D = 1 (Std.) | 35 | 30 | 30.5 | 30 | 30 | 35
Elbow 90°- Threaded/Screwed R/D = 1.5 (LR) | Elbow 90° | Threaded/Screwed | R/D = 1.5 (LR) |  | 16 | 14 | 13 | 20 | 20
Elbow 90°- Welded/Flanged R/D = 1 (Std.) | Elbow 90° | Welded/Flanged | R/D = 1 (Std.) |  | 20 |  |  |  | 20
Elbow 90°- Welded/Flanged R/D = 2 (LR) | Elbow 90° | Welded/Flanged | R/D = 2 (LR) |  | 17 |  |  |  | 17
Elbow 90°- Welded/Flanged R/D = 4 (LR) | Elbow 90° | Welded/Flanged | R/D = 4 (LR) |  | 14 |  |  |  | 14
Elbow 90°- Welded/Flanged R/D = 6 (LR) | Elbow 90° | Welded/Flanged | R/D = 6 (LR) |  | 12 |  |  |  | 12
Elbow- Mitered 1 weld 90° | Elbow | Mitered 1 weld | 90° |  | 60 |  |  | 58 | 60
Elbow- Mitered 2 welds 45° | Elbow | Mitered 2 welds | 45° |  | 15 |  |  |  | 15
Elbow- Mitered 3 welds 30° | Elbow | Mitered 3 welds | 30° |  | 8 |  |  |  | 8
Elbow- Street Elbow (Male to Female) 90° | Elbow | Street Elbow (Male to Female) | 90° |  |  |  |  | 50 | 50
Elbow- Street Elbow (Male to Female) 45° | Elbow | Street Elbow (Male to Female) | 45° |  |  |  |  | 26 | 26
Elbow 45°- Threaded/Screwed R/D = 1 (STD) | Elbow 45° | Threaded/Screwed | R/D = 1 (STD) | 17 |  | 16 | 16 | 16 | 17
Elbow 45°- Threaded/Screwed R/D = 1.5 (LR) | Elbow 45° | Threaded/Screwed | R/D = 1.5 (LR) |  |  |  | 10 |  | 10
Elbow 45°- Welded/Flanged R/D = 1 (STD) | Elbow 45° | Welded/Flanged | R/D = 1 (STD) | [5 empty] | 10
Elbow 45°- Welded/Flanged R/D = 2 (LR) | Elbow 45° | Welded/Flanged | R/D = 2 (LR) | [5 empty] | 8.5
Elbow 45°- Welded/Flanged R/D = 4 (LR) | Elbow 45° | Welded/Flanged | R/D = 4 (LR) | [5 empty] | 7
Elbow 45°- Welded/Flanged R/D = 6 (LR) | Elbow 45° | Welded/Flanged | R/D = 6 (LR) | [5 empty] | 6
Elbow 45°- Mitered 1 weld | Elbow 45° | Mitered 1 weld |  |  | 15 |  |  | 15 | 15
Elbow 45°- Mitered 2 welds | Elbow 45° | Mitered 2 welds |  |  | 6 |  |  |  | 6
Elbow 45°- Mitered 3 welds | Elbow 45° | Mitered 3 welds | [6 empty] | 4
Tee- T-Through branch (Main-main Converge/Main-main Diverge) | Tee | T-Through branch (Main-main Converge/Main-main Diverge) |  |  | 60 | 60 | 60 | 60 | 60
Tee- T-Through run (Main-branch Converge/Diverge) | Tee | T-Through run (Main-branch Converge/Diverge) |  |  | 20 |  | 10 | 20 | 20
Tee- T-Through as an elbow (Capped) | Tee | T-Through as an elbow (Capped) |  |  | 20 |  |  |  | 20
Gate Valve (Full Open/Straight Way) | Gate Valve (Full Open/Straight Way) |  |  |  | 8 | 8 | 8 | 13 | 13
Gate Valve (Half Open - Not recommended) | Gate Valve (Half Open - Not recommended) | [6 empty] | 260 | 260
Gate Valve (1/4 Open - Not recommended) | Gate Valve (1/4 Open - Not recommended) | [6 empty] | 900 | 900
Alarm/Check Valve (Swing Type) | Alarm/Check Valve (Swing Type) |  |  |  | 100 | 50 |  | 50 | 100
Alarm/Check Valve (Mushroom Type) | Alarm/Check Valve (Mushroom Type) |  |  |  |  | 250 |  |  | 250
Lift Check Valve | Lift Check Valve |  |  |  | 600 |  |  |  | 600
Butterfly Valve | Butterfly Valve |  |  |  |  | 45 |  | 40 | 45
Globe Valve (Full Valve) | Globe Valve (Full Valve) |  |  |  | 340 | 330 | 320 | 340 | 340
Globe Valve (Y Pattern 60 degrees) | Globe Valve (Y Pattern 60 degrees) | [6 empty] | 175 | 175
Globe Valve (Y Pattern 45 degrees) | Globe Valve (Y Pattern 45 degrees) | [6 empty] | 145 | 145
Ball Valve (Full Bore) | Ball Valve (Full Bore) |  |  |  | 3 |  | 3 |  | 3
Ball Valve (Reduced Bore) | Ball Valve (Reduced Bore) | [5 empty] | 25 |  | 25
Plug valve (Branch Flow) | Plug valve (Branch Flow) |  |  |  | 90 |  |  |  | 90
Plug valve (Flow through) | Plug valve (Flow through) |  |  |  | 18 |  |  |  | 18
Plug valve (Three Way Flow Through) | Plug valve (Three Way Flow Through) |  |  |  | 30 |  |  |  | 30
Hose Coupling | Hose Coupling |  |  |  | 5 |  |  |  | 5
Angle valve (45 degree) | Angle valve (45 degree) |  |  |  | 55 |  |  |  | 55
Angle valve (90 degree) | Angle valve (90 degree) |  |  |  | 150 |  |  | 145 | 150
Cock valve (Straight) | Cock valve (Straight) | [6 empty] | 18 | 18
Cock valve (3-way straight flow) | Cock valve (3-way straight flow) | [6 empty] | 44 | 44
Cock valve (3-way branch) | Cock valve (3-way branch) | [6 empty] | 140 | 140
Foot valve (Strainer & poppet) | Foot valve (Strainer & poppet) | [6 empty] | 420 | 420
Foot valve (Leather hinged) | Foot valve (Leather hinged) | [6 empty] | 75 | 75
Return Bend | Return Bend | [6 empty] | 50 | 50

## C-Value
VALUE OF C (Adapted from MS1910:2006 pg. 76)
TYPE OF PIPE | C value
General Metal (Extremely smooth) | 130
Cast Iron (CI) | 100
Cast Iron Cement Lined (CICL) | 130
Cast Iron Bituminous Lined (CIBL) | 130
Cast Iron (Asphalt Coated) | 100
Ductile Iron (DI) | 110
Ductile Iron Cement Lined (DICL) | 130
Mild Steel (MS) | 120
Mild Steel Cement Lined (MSCL) | 130
Galvanised Iron (GI) | 120
Stainless steel | 140
Steel | 100
Steel (Corrugated) | 60
Copper (Cu) | 140
Aluminium (Al) | 130
Brass (Br) | 130
Lead | 130
Tin | 130
Corrugated metal | 60
Reinforced glass fibre (FRP) | 140
Plastic (General) | 130
High-density polyethylene (HDPE) | 150
Acrylonite Butadiene Styrene (ABS) | 130
Polyethylene (PE) | 140
Polyvinyl chloride (PVC, CPVC) | 150
Spun Cement | 130
Concrete | 100
Vitrified clay | 110
Wooden | 110
Masonry | 110
Glass | 130